## Instructions
SACRIFICIAL ANODE DESIGN CALCULATION Version 1.0, 9 November 2012
General Information | 1. This sheet can be used as an design aid to design sacrificial anode systems for marine structures like harbour steel structures, fixed steel offshore structures etc. 2. User is advised to be acquainted with DNV or EN or other relevant standard for sacrificial anode design before using this design aid. 3. Design steps, their descriptions, and notes on using this design aid can be found below. 4. Colored boxes are found in the 'design sheet' tab wherein the user can select/enter data to complete the design. Please read further about the colored boxes below. 5. Please read copyright statement below. 6. Please read disclaimer statement below.
Design Steps
Notes while using the design aid | Select the applicable design standard, climatic region, depth range, seawater resistance, design life, design protection potential. Foreign data entry is supported for design standard, climatic region, depth range, seawater resistance and design life allowing the user to enter custom data. No foreign data entry is allowed for design protection potential. In case of custom data entry, the current density values will then need to be entered manually into the orange boxes. | Enter the surface area values in the purple box. The user may enter surface area based on bare/coated area as well as according to exposure type (tidal/ immersed/ buried). If only part of user's immersed structure is coated, the user need to enter the corresponding areas in "immersed coated surface area" and "immersed bare surface area". This design aid does not calculate surface area. The surface area calculation shall be done by user and seperately entered into the sheet. User is advised to follow definition of extended tidal zone and sediment surface area in EN or DNV standards. Cell comments have been provided for extended tidal zone surface area. | Select the coating category. The sheet automatically selects and calculates coating breakdown factors. After this step, the design sheet would have calculated the anode current requirements (initial, mean and final). | Select the anode material, environment and the type of anode. A list of standard anodes from BAC Denmark is available in the library for the user to select from. Foreign data entry is supported allowing the user to choose a custom anode. In case of custom entry, the user will need to enter the weight and dimensions of the anode in the "anode data" sheet,. If an aluminium anode then data shall be entered in the yellow line and if zinc in the green line. No foreign data entry is allowed for anode material or anode environment. User is advised to refer EN or DNV standards for deeper understanding of the anode selection paramters. Anode type cell displays some information on anode (mounting) type. | After selecting the type of anodes, the required number are automatically calculated and shown on the "Results" box. The number of anodes is determined by 3 requirements - intial current, final current and weight requirement. All 3 requirements must be met in the design, and therefore the number of anodes to be installed, is the highest number of anodes from the 3 requirements. This number is shown at the bottom line as "No. of anodes selected for cathode zone". The design of the system may be iterative - choosing a particular anode, determining whether it meets the requirements, and repeating if necessary. | Reiterate the anode selection step as required to obtain the optimum number of anodes and produce an anode arrangement drawing. Please note this design aid will not suggest how best to distribute anodes. This shall be done by the responsible engineer as this involves more than distributing the anodes uniformly. | The user is asked to contact jaja@cowi.dk to have a guidance on who to contact for quality check on the sacrificial anode selection design. This also applies to evaluation of corrosion situation, selection of strategy, design report, anode specification data, drawing arrangement etc as part of the sacrificial anode design.
Colored boxes in the design aid | There are blue, orange and purple boxes in the 'design sheet tab'. The user can also find useful input messages or cell comments for certain boxes. Somtimes error messages are displayed to guide the user to data entry. Blue boxes are drop-down lists which the user can use to select design parameters. While some blue drop-down lists restrict the user in entering foreign data, most of the blue drop-down lists allow foreign data to be entered, thus allowing for deviation from the standards library. In such cases, the user will be guided by informative error messages or cell comments. Orange boxes normally gets auto-filled. In cases of deviation (or foreign data being entered in blue boxes), the parameters for orange boxes will need to be entered manually by the user. In some cases, the orange boxes can show error (#VALUE) if there is a mismatch between standard selected and related data. In such cases, information will be found on the related blue box. Purple boxes are intended for the user to enter the surface area calculation. The surface area calculation shall be done by user and seperately entered into the purple boxes.
Copyright statement | Copyright © 2012 COWI Cathodic Protection Network. COWI Group Concrete and Corrosion Network grants permission of this design aid for COWI internal use only. A copy of this notice must be appended to any print of this sheet taken. Distribution or sharing with external customers is allowed only in pdf format. Distiribution or sharing for any other purpose is prohibited. Copying or uploading for any purpose is prohibited.
Disclaimer statement | COWI Group Concrete and Corrosion Network cannot be held responsible for the outcome or consequences of actions taken on the basis of using this design tool. The use is subject to QA following COWI's general procedures For cathodic protection assistance and more information, contact jaja@cowi.dk

## GACP Calculation
Galvanic Anode Cathodic Protection
Design Calculation
Norm options: EN 12495:2000, DNV-RP-B401:2021, Norsok M-503:2007 |  |  |  | Ver. 4.0 | Authorized Practice
Case: | Shinan-Ui OWF - Basic design (Detailed design phase I) |  |  | Case No. | A242416
Subject: | Deep cluster (cluster 1) |  |  | Date: | 2023-11-17
Prep'd: | BOHR | Checked: | Appr'd:
DESIGN STANDARD, CLIMATIC CONDITIONS
Design Standard |  | DNV-RP-B401:2021
Climatic Region |  | Sub-Tropical "12-20c"
Depth Range (m) |  | "0-20"
DEPTH RANGE, SEAWATER RESISTANCE, DESIGN LIFE AND DESIGN PROTECTION POTENTIAL
Seawater Resistance |  |  |  | 0.26 | ohm-m | pø
Design Life |  |  |  | 25 | yrs | tf
Design Protection Potential |  |  |  | -0.8 | V | Ec
SURFACE AREA OF STRUCTURE
Extended Tidal Zone Bare Surface Area |  |  |  | 0 | m2 | Act
Extended Tidal Zone Coated Surface Area |  |  |  | 0 | m2 | Actc
Immersed Zone Bare Surface Area |  |  |  | 65.9734 | m2 | Ac
Immersed Zone Coated Surface Area |  |  |  | 2193.1714 | m2 | Acc
Mudline Zone Bare Surface Area |  |  |  | 0 | m2 | Acm
Mudline Zone Coated Surface Area |  |  |  | 0 | m2 | Acmc
Sediment Zone Bare Surface Area |  |  |  | 1143.5397 | m2 | Acs
Sediment Zone Coated Surface Area |  |  |  | 0 | m2 | Acsc
COATING CATEGORY
Coating system of Cathode Zone |  |  |  | "Category IV"
ANODE SELECTION
Anode Material |  |  |  | Aluminium
Anode Environment |  |  |  | seawater
Choose Anode by name |  |  |  | Platform 350 kg
Anode Material selected |  |  |  | Aluminium
Weight of Selected Anode |  |  |  | 350 | kg | ma,i
Anode Type |  |  |  | Type 1
Anode to Cathode Distance |  |  |  | >0.30 | m
Utlization Factor |  |  |  | 0.9 |  | u
Electrochemical Capacity |  |  |  | 2000 | A-hr/kg | ε
Closed Circuit Potential |  |  |  | -1.05 | V | Ea
RESULTS
No. of anodes required by weight |  |  |  | 18 | ea
No. of anodes to meet initial current requirement |  |  |  | 8 | ea
No. of anodes to meet final current requirement |  |  |  | 20 | ea
Anodes selected for cathode zone |  |  |  | 20 | ea
Weight of each selected anode |  |  |  | 350 | kg
Total weight of anodes |  |  |  | 7000 | kg
CURRENT DENSITIES
Tidal initial current density |  |  |  | 0.17 | A/m2 | Iticd
Tidal mean current density |  |  |  | 0.08 | A/m2 | Itmcd
Tidal final current density |  |  |  | 0.11 | A/m2 | Itfcd
Immersed initial current density |  |  |  | 0.17 | A/m2 | Iicd
Immersed mean current density |  |  |  | 0.08 | A/m2 | Imcd
Immersed final current density |  |  |  | 0.11 | A/m2 | Ifcd
Mudline initial current density |  |  |  | 0.02 | A/m2 | Imicd
Mudline mean/final current density |  |  |  | 0.02 | A/m2 | Immfcd
Sediment initial current density |  |  |  | 0.02 | A/m2 | Isicd
Sediment mean/final current density |  |  |  | 0.02 | A/m2 | Ismfcd
COATING BREAKDOWN FACTORS
Initial Coating breakdown factor, submerged zone |  |  |  | 0.02 |  | asub, fcsi
Initial Coating breakdown factor, mudline zone |  |  |  | 0.1 |  | amud, fcmi
Initial Coating breakdown factor, sediment zone |  |  |  | 0.1 |  | ased, fcsei
Annual depletion rate |  |  |  | 0.008 |  | b
Mean Coating breakdown factor, submerged zone |  |  |  | 0.12 |  | fcsm
Final Coating breakdown factor, submerged zone |  |  |  | 0.22 |  | fcsf
Mean Coating breakdown factor, mudline zone |  |  |  | 0.2 |  | fcmm
Final Coating breakdown factor, mudline zone |  |  |  | 0.3 |  | fcmf
Mean Coating breakdown factor, sediment zone |  |  |  | 0.2 |  | fcsem
Final Coating breakdown factor, sediment zone |  |  |  | 0.3 |  | fcmsef
CURRENT REQUIREMENTS
Initial Current Requirement |  |  |  | 41.5431 | A | Ii
Mean Current Requirement |  |  |  | 49.2031 | A | Im
Final Current Requirement |  |  |  | 83.2026 | A | If
ANODE DIMENSIONS
Length of Anode (Top) |  |  |  | 3.025 | m | La,t
Length of Anode (Bottom) |  |  |  | 2.975 | m | La,b
Height of Anode |  |  |  | 0.213 | m | Ha
Width of Anode (Top) |  |  |  | 0.26 | m | Wa,t
Width of Anode (Bottom) |  |  |  | 0.287 | m | Wa,b
Insert Width / Diameter |  |  |  | 0.1413 | m | Wis
Insert Thickness |  |  |  | 3.1416 | m | Tis
ANODE CALCULATIONS
Net weight of Anode selected |  |  |  | 350 | kg | ma,i
Min. weight of Anode Required |  |  |  | 5986.3791 | kg
Equivalent Anode Radius |  |  |  | 0.15486 | m | ra
Specific Density of Anode Material |  |  |  | 2700 | kg/m3
Final Mass of Anode |  |  |  | 35 | kg
Final Volume of Anode |  |  |  | 0.055302 | m3
Final Radius of Anode |  |  |  | 0.080744 | m
Anode (individual) initial resistance |  |  |  | 0.04621 | ohm | Rai
Anode (individual) final resistance |  |  |  | 0.05971 | ohm | Raf
Anode (individual) initial current output |  |  |  | 5.4101 | A | Iai
Anode (individual) final current output |  |  |  | 4.1869 | A | Iaf
Note on H14: See sheet named "Seawater resistivity" for more information.
Note on H19: Please leave the value as zero if using standard other than EN 12495.
Note on H20: Please leave the value as zero if using standard other than EN 12495.
Note on H29: Category I One layer of epoxy paint coating, min. 20 µm nominal DFT Category II One or more layers of marine paint coating, total nominal DFT min. 250 µm Category III Two or more layers of marine paint coating, total nominal DFT min. 350 µm Category IV Two or more layers of epoxy-based coatings according to NORSOK M-501 systems 3B or 7, with total nominal DFT of minimum 350 μm or the equivalent and meeting all requirements for coating system qualification, coating application, inspection and repairs given in the same standard. The purchaser is further required to be involved in quality control by accepting the coating application procedure and carrying out quality surveillance during coating work.
Note on H87: If the insert is circular, please note the cell value will/ need to correspond to PI()

## Surface areas overview
| Cluster | Pile length (embedded) | Piles (embedded, bare steel) | Pile stick-up (immersed, bare steel) | Piles (immersed, bare steel) | J-tubes (immersed, coated) | Boat landing (immersed, coated) | Jacket (immersed, coated)
WTG01 | 2 | 50.5 | 2221.106 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG02 | 3 | 43 | 1891.2388 | 1.5 | 65.9734 | 80.1644 | 98.069 | 1144.4028
WTG03 | 1 | 54 | 2375.044 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG04 | 2 | 52 | 2287.0795 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG05 | 2 | 52 | 2287.0795 | 1.6 | 70.3717 | 113.3953 | 99.056 | 1718.4547
WTG06 | 2 | 47.5 | 2089.1591 | 1.6 | 70.3717 | 113.3953 | 99.056 | 1718.4547
WTG07 | 2 | 48.5 | 2133.1414 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG08 | 3 | 46 | 2023.1857 | 1.5 | 65.9734 | 80.1644 | 98.069 | 1144.4028
WTG09 | 3 | 52 | 2287.0795 | 1.5 | 65.9734 | 80.1644 | 98.069 | 1144.4028
WTG10 | 1 | 46 | 2023.1857 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG11 | 1 | 36 | 1583.3627 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG12 | 1 | 41 | 1803.2742 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG13 | 2 | 39.5 | 1737.3007 | 3.8 | 167.1327 | 113.3953 | 99.056 | 1718.4547
WTG14 | 2 | 34 | 1495.3981 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG15 | 2 | 62 | 2726.9024 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG16 | 3 | 45.5 | 2001.1945 | 1.5 | 65.9734 | 80.1644 | 98.069 | 1144.4028
WTG17 | 2 | 29.5 | 1297.4778 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG18 | 1 | 38 | 1671.3273 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG19 | 1 | 57 | 2506.9909 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG20 | 1 | 54.5 | 2397.0352 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG21 | 1 | 49.5 | 2177.1237 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022
WTG22 | 2 | 44.5 | 1957.2122 | 3.4 | 149.5398 | 113.3953 | 99.056 | 1718.4547
WTG23 | 2 | 47.5 | 2089.1591 | 1.5 | 65.9734 | 113.3953 | 99.056 | 1718.4547
WTG24 | 3 | 58.5 | 2572.9644 | 1.9 | 83.5664 | 80.1644 | 98.069 | 1144.4028
WTG25 | 3 | 44.5 | 1957.2122 | 1.5 | 65.9734 | 80.1644 | 98.069 | 1144.4028
WTG26 | 1 | 26 | 1143.5397 | 1.5 | 65.9734 | 129.4288 | 94.6404 | 1969.1022

## Surface area
COMPONENT | SURFACE AREA (m.sq.)
| CLUSTER-1 | CLUSTER-2 | CLUSTER-3
WTG NO | 19 | 1 | 24
JACKET (from DL to top of pile) | 1969.1022 | 1718.4547 | 1144.4028
BOAT LANDING (from Dl and below) | 94.6404 | 99.056 | 98.069
J-TUBE (from Dl and below) (2 NO'S) | 129.4288 | 113.3953 | 80.1644
Pile stick up diameter
|  |  |  | 3.5 | m

## Input Parameters
Standard | Seawater Resistance | Anode Material | Environment | Protection Potential | Depth (m) | Coating Category | Anode to Object Distance | Life | Climatic Region
DNV-RP-B401:2021 | 0.15 | Aluminium | seawater | -0.8 | "0-20" | "Bare" | <0.15 | 5 | Artic "<7c"
EN 12495:2000 | 0.2 | Zinc | sediment | -0.9 | ">20-30" | "Category I" | 0.15 - 0.30 | 10 | Temperate "7-12c"
Norsok M-503: 2007 | 0.25 |  |  |  | ">30-100" | "Category II" | >0.30 | 15 | Sub-Tropical "12-20c"
| 0.3 |  |  |  | ">100-300" | "Category III" |  | 20 | Tropical ">20c"
[5 empty] | ">300" | "Category IV" |  | 25 | North Sea (northern sector) above 62° N
[8 empty] | 30 | North Sea (northern sector) 55°N to 62°N
North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands
Arabian Gulf, India, Australia, Brazil, West Africa
Anode Material | Environment | Design Standard | [6 empty] | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia
Aluminium | seawater | DNV-RP-B401:2021 | [6 empty] | North Sea (Up to 62 °N)
Norwegian Sea (above 62 °N)
Anode Material | Environment | Design Standard | Electrochemical Capacity (Ah/Kg) | Closed Circuit Potential (V)
Aluminium | seawater | DNV-RP-B401:2021 | 2000 | -1.05
Aluminium | sediment | DNV-RP-B401:2021 | 1500 | -1
Zinc | seawater | DNV-RP-B401:2021 | 780 | -1.03
Zinc | sediment | DNV-RP-B401:2021 | 750 | -0.98
Aluminium | seawater | Norsok M-503: 2007 | 2000 | -1.05
Aluminium | sediment | Norsok M-503: 2007 | 1730 | -1
Zinc | seawater | Norsok M-503: 2007 | 780 | -1.03
Zinc | sediment | Norsok M-503: 2007 | 750 | -0.98
Aluminium | seawater | EN 12495:2000 | 2500 | -1.09
Aluminium | sediment | EN 12495:2000 | 2000 | -1.05
Zinc | seawater | EN 12495:2000 | 780 | -1.03
Zinc | sediment | EN 12495:2000 | 750 | -0.99
Anode Material | Specific Density (kg/m3)
Aluminium | 2700
Zinc | 6920
Anode Type | Description | Utilization Factor | Resistance Formula
Type 1 | Long slender stand-off anode; L ≥ 4r | 0.9 | Ra = (ρ/(2πL))(ln(4L/r)-1)
Type 2 | Short slender stand-off anode; L < 4r | 0.85 | Ra = (ρ/(2πL))(ln[2l/r(1+√(1+(r/2L)2)] +r/2L - √(1+(r/2L)2)
Type 3 | Long flush mounted L ≥ 4 width and L ≥ 4 thickness | 0.85 | Ra = ρ / (2S)
Type 4 | Short flush mounted, bracelet and other flush mounted shapes | 0.8 | Ra = 0.315ρ / √A

## Anode Resistance Sheet
Anode Name | Initial Length of Anode | Anode (individual) initial resistance | Final Lenght of Anode | Insert Volume | Final Mass of Anode | Specific Density | Final Volume of anode Vaf | Final Radius of Anode rf | Anode (individual) final resistance
Platform 350 kg | 3 | 0.04621 | 2.7 | 0.042339 | 35 | 2700 | 0.055302 | 0.080744 | 0.05971
Type | Utilization Factor | Initial Resistance | Final Length | Final Mass | Final Volume of anode mass | Final Radius | Final Resistance | Correction Factor
Type 1 | 0.9 | 0.04621 | 2.7 | 35 | 0.055302 | 0.080744 | 0.05971 | 1
Type 2 | 0.85 | 0.046564 | 2.7 | 52.5 | 0.061783 | 0.085345 | 0.059939 | 1
Type 3 | 0.85 | 0.079426 | 2.7 | 52.5 | 0.061783 | 0.085345 | 0.090862 | 1
Type 4 | 0.8 | 0.055519 | 3 | 70 | 0.068265 | 0.15486 | 0.055519 | 1

## Anode Data
*only guidance depends on insert
Anode Name | Material | Net weight (kg) | Gross weight (kg)* | Anode Length Top La,t (mm) | Anode Length Bottom La,b (mm) | Anode Width Top Wa,t (mm) | Anode Width Bottom Wa,b (mm) | Anode Height Ha (mm) | Insert Width (mm) | Insert Thickness (mm) | Supplier | Checked 07-01-2016 (PHNI) | Checket 17-06-2016 (RSO) | kontrol af vægt af anode | ændret dec. 17 | Control of anode weight
15-AL | Aluminium | 1.2 | 1.5 | 160 | 215 | 60 | 95 | 30 | 25 | 5 | BAC | ok |  | 1.1767 | nej, tegning
User defined (Al) | Aluminium | 350 | 436 | 2675 | 2725 | 260 | 287 | 210 | 114 | 3447 | [5 empty] | 417.6402
User defined (Zn) | Zinc | [14 empty] | 0
25-AL | Aluminium | 2.1 | 2.5 | 205 | 265 | 75 | 115 | 34 | 25 | 5 | BAC | C changed from 2,00 to 2,10 | ok | 2.0491 | nej, tegning
43-AL | Aluminium | 3.6 | 4.1 | 245 | 340 | 110 | 150 | 35 | 30 | 5 | BAC | ok |  | 3.593 | nej, tegning
60-AL | Aluminium | 5.2 | 6 | 420 | 570 | 60 | 110 | 43 | 30 | 5 | BAC | ok |  | 4.8845 | nej, tegning
80-AL | Aluminium | 7.5 | 8 | 240 | 350 | 115 | 150 | 62 | 30 | 5 | BAC | ok |  | 6.5428 | nej, tegning
90-AL | Aluminium | 7.8 | 9 | 780 | 930 | 60 | 110 | 40 | 30 | 5 | BAC | ok |  | 7.8485 | nej, tegning
93-AL | Aluminium | 7.9 | 9.3 | 870 | 960 | 60 | 110 | 37 | 30 | 5 | BAC | ok |  | 7.7693 | nej, tegning
114-AL | Aluminium | 10.6 | 11.4 | 455 | 600 | 70 | 120 | 79 | 30 | 5 | BAC | ok |  | 10.6886 | nej, tegning
170-AL | Aluminium | 15.8 | 17 | 780 | 950 | 60 | 120 | 75 | 30 | 5 | BAC | F changed from 960 to 950 | ok | 15.7642 | nej, tegning
175 AL | Aluminium | 16.1 | 17.5 | 875 | 960 | 60 | 120 | 75 | 30 | 5 | BAC | ok |  | 16.721 | nej, tegning
350-AL | Aluminium | 29.5 | 35 | 1780 | 1920 | 120 | 70 | 68 | 30 | 5 | BAC | C changed from 31,6 to 29,5, E is not present in drawing | ok, E estimeret til 1780 | 32.2673 | nej, tegning
399-AL | Aluminium | 33.3 | 39.9 | 2320 | 2500 | 70 | 105 | 60 | 40 | 10 | BAC | K changed from 10 to 15 | no changed to 10 | 34.1607 | nej, tegning
Bera 20 | Zinc | 1.9 | 2 | 80 | 165 | 60 | 90 | 30 | 25 | 5 | BAC | K and L not on drawing |  | 1.9065 | nej, tegning
Bera 22 | Zinc | 2.1 | 2.2 | 230 | 300 | 77 | 77 | 32 | 25 | 5 | BAC | K and L not on drawing |  | 4.5176 | nej, tegning
Bera 35 | Zinc | 3.2 | 3.5 | 186 | 220 | 60 | 96 | 30 | 30 | 5 | BAC | K and L not on drawing |  | 3.2861 | nej, tegning
Bera 55 | Zinc | 5.1 | 5.5 | 215 | 260 | 80 | 113 | 33 | 30 | 5 | BAC | C changed from 22,2 to 21,5, K and L not on drawing | ok | 5.2327 | nej, tegning
Bera 102 | Zinc | 9.3 | 10.2 | 260 | 350 | 126 | 150 | 33 | 40 | 10 | BAC | no drawing, no changes |  | 2.7556 | ændret anodegeometri, der findes ikke tegning
Bera 155 | Zinc | 14.7 | 15.5 | 450 | 590 | 70 | 116 | 45 | 30 | 5 | BAC | no drawing, no changes |  | 4.9557 | ændret anodegeometri, der findes ikke tegning
Bera 235 | Zinc | 21.5 | 23.5 | 820 | 950 | 60 | 120 | 40 | 40 | 10 | BAC | E changed from 1457 to 1500, F changed from 1525 to 1550, K has according to drawing 3" = 76mm --> K changed from 50 to 76 | ok | 5.6824 | nej, tegning
Platform 85 kg | Aluminium | 85 | 97 | 1100 | 1100 | 160 | 193 | 177 | 60 | 3141.5927 | BAC | no drawing, no changes |  | 85.637 | nej
Platform 97 kg | Aluminium | 97 | 124 | 1300 | 1300 | 160 | 193 | 170 | 50 | 3141.5927 | BAC | D changed from 335 to 333,5, E changed from 3480 to 2730, F changed from 3520 to 2770, J changed from 114,3 (4,5") to 101,6 (4") | ok | 99.8838 | ja, insert
Platform 102 kg | Aluminium | 102 | 127 | 1500 | 1550 | 160 | 192 | 175 | 76 | 3141.5927 | BAC | no drawing, J should be the same as for the 626 anode therfore changed from 114,3 to 101,6 | ok | 109.7422 | ja, insert og anodegeometri
Platform 132 kg | Aluminium | 132 | 162 | 2390 | 2430 | 130 | 167 | 160 | 76 | 3141.5927 | BAC | D changed from 705 to 704,5, E changed from 3475 to 2975, F changed from 3525 to 3025, G chnaged from 275 to 265, J changed from 114,3 to 101,6 | ok | 126.9407 | ja, insert
Platform 240 kg | Aluminium | 240 | 333.5 | 2730 | 2770 | 190 | 227 | 207 | 114.13 | 3141.5927 | BAC | A changed from AP 3300 to 3300XP according to homepage, J changed from 114,3 to 100 |  | 248.1213 | ja, insert ( 4 tommer rør)
Platform 350 kg | Aluminium | 350 | 436 | 3025 | 2975 | 260 | 287 | 213 | 141.3 | 3141.5927 | BAC | J changed from 114,3 to 101,6 |  | 349.9623 | ja, insert ( 4 tommer rør)
Platform 626 kg | Aluminium | 626 | 704.5 | 2975 | 3025 | 265 | 315 | 295 | 114.3 | 3141.5927 | BAC | no values to D --> take 390 out, J changed from 114,3 to 101,6 |  | 618.877 | ja, insert ( 4 tommer rør)
3300XP | Aluminium | 330 | 390 | 2372 | 2372 | 252 | 252 | 244 | 114.3 | 3141.5927 | Impalloy | no values to D --> take 390 out, J changed from 114,3 to 101,6 |  | 332.9397 | ja, insert ( 4 tommer rør)
AS 3170 | Aluminium | 246 |  | 2350 | 2350 | 245 | 245 | 250 | 114.3 | 3141.5927 | ETC | J changed from 114,3 to 101,6 |  | 328.3193 | nej
AS 4085 | Aluminium | 330 |  | 3000 | 3000 | 225 | 225 | 225 | 114.3 | 3141.5927 | ETC | J changed from 50 to 20 |  | 331.7935 | nej
AS 4150 | Aluminium | 330 |  | 2440 | 2440 | 252 | 252 | 244 | 114.3 | 3141.5927 | ETC | J chnagewd from 50 to 25 |  | 342.4844 | nej
AS 6500 | Aluminium | 570 |  | 3000 | 3000 | 280 | 280 | 287 | 114.3 | 3141.5927 | ETC | J changed from 50 to 20 |  | 576.2152 | nej
ASOE350 | Aluminium | 35 |  | 1300 | 1300 | 101 | 101 | 101 | 20 | 3141.5927 | Syncor | J changed from 50 to 20 |  | 35.2169 | nej
ASOE800 | Aluminium | 80 |  | 2360 | 2360 | 114 | 114 | 114 | 25 | 3141.5927 | Syncor | J chnagewd from 50 to 25 |  | 80.8631 | nej
ASOE500 | Aluminium | 50 |  | 1300 | 1300 | 120 | 120 | 120 | 20 | 3141.5927 | Syncor | J changed from 50 to 60,3 |  | 50.1738 | nej
ASOE680 | Aluminium | 68 |  | 1520 | 1520 | 133 | 133 | 127 | 20 | 3141.5927 | Syncor |  |  | 69.0392 | nej
ASOE1190 | Aluminium | 119 |  | 1525 | 1525 | 184 | 184 | 159 | 25 | 3141.5927 | Syncor | I is only 10 on homepage, must be a mistake there |  | 120.1951 | nej
ASOE1480 | Aluminium | 148 |  | 2373 | 2373 | 160 | 160 | 162 | 60.3 | 3141.5927 | Syncor | D is not given therfore 390 has been taken out |  | 149.964 | nej
ASOE1750 | Aluminium | 175 |  | 2500 | 2500 | 190 | 190 | 190 | 114.3 | 3141.5927 | Syncor | ok |  | 176.9983 | nej
ASOE2400 | Aluminium | 240 |  | 2622 | 2622 | 210 | 210 | 210 | 114.3 | 3141.5927 | Syncor | ok |  | 243.1101 | nej
ASOE3300 | Aluminium | 330 |  | 2372 | 2372 | 252 | 252 | 244 | 114.3 | 3141.5927 | Syncor | ok |  | 328.0793 | nej
ASOE4350 | Aluminium | 435 |  | 2910 | 2910 | 254 | 254 | 257 | 114.3 | 3141.5927 | Syncor | D changed from 27,3 to 27,2 | ok | 432.2699 | nej
ASOE5650 | Aluminium | 565 |  | 2973 | 2973 | 283 | 283 | 283 | 114.3 | 3141.5927 | Syncor | ok |  | 560.5177 | nej
224 HAL | Aluminium | 18.5 | 22.4 | 723 | 777 | 80 | 115 | 100 | 25 | 3141.5927 | BAC | ok |  | 18.7139 | nej
280 HAL | Aluminium | 21.5 | 27.3 | 945 | 1000 | 80 | 112 | 90 | 25 | 3141.5927 | BAC | ok |  | 21.3611 | nej
385 HAL | Aluminium | 30 | 37.7 | 1346 | 1400 | 80 | 112 | 90 | 25 | 3141.5927 | BAC | ok |  | 30.1738 | nej
427 HAL | Aluminium | 35 | 42.7 | 1475 | 1525 | 80 | 113 | 95 | 25 | 3141.5927 | BAC | ok |  | 35.1072 | nej
516 HAL | Aluminium | 40 | 51.6 | 1980 | 2020 | 80 | 110 | 85 | 25 | 3141.5927 | BAC | ok |  | 40.9278 | nej
485 HAL | Aluminium | 40 | 47.7 | 1380 | 1435 | 85 | 130 | 105 | 25 | 3141.5927 | BAC | ok |  | 40.9934 | nej
527 HAL | Aluminium | 45 | 52.7 | 1475 | 1525 | 90 | 133 | 104 | 25 | 3141.5927 | BAC | F changed from 1525 to 1520 | ok | 44.9426 | nej
566 HAL | Aluminium | 45 | 56.6 | 2210 | 2250 | 80 | 110 | 85 | 25 | 3141.5927 | BAC | not found |  | 45.6375 | nej
616 HAL | Aluminium | 50 | 61.6 | 2440 | 2480 | 80 | 110 | 85 | 25 | 3141.5927 | BAC | F changed from 1525 to 1520 | ok | 50.3473 | nej
585 HAL | Aluminium | 50 | 57.7 | 1480 | 1520 | 90 | 140 | 110 | 25 | 3141.5927 | BAC | ok |  | 49.218 | nej
Beralin | Aluminium | 54.53 |  | 1420 | 1420 | 120 | 120 | 120 | 25 | 3141.5927 | BAC | ok |  | 53.3276 | nej
625 HAL | Aluminium | 54.8 | 62.5 | 1480 | 1520 | 90 | 145 | 120 | 25 | 3141.5927 | BAC | not found | ok, drw included | 55.0905 | nej
666 HAL | Aluminium | 55 | 66.6 | 2440 | 2480 | 80 | 112 | 90 | 25 | 3141.5927 | BAC | ok |  | 54.1 | nej
716 HAL | Aluminium | 60 | 71.6 | 2475 | 2525 | 80 | 114 | 97 | 25 | 3141.5927 | BAC
750 HAL | Aluminium | 75 | 86.6 | 2475 | 2525 | 85 | 125 | 105 | 25 | 3141.5927 | BAC
816 HAL | Aluminium | 70 | 81.6 | 2475 | 2525 | 85 | 129 | 102 | 25 | 3141.5927 | BAC

## Seawater Resistivity
Resistivity
This sheet will give a short introduction to how seawater resistivity is calculated using DNV-RP-B401, and list our values from known areas.
Resistivity of Sea water are influeced by several factors, but the two primary factors are salinity and temperature. DNV-RP-B401 has a figure with corrolates some of the often used temperatures and salinities. The figure is listed below.
It is very important when calculating sacrificial anodes that you uses the highest resistivity for the given area. If not, then the calculated anodes may not be able to protect the structure. The resistivity of seawater varies over time. The seasonal variations may be large, for instance in the Baltic, the resistivity increases during spring because of the increase in melting snow and ice from the region, which makes the water more brackish.
List of references with resistivity.
Project description | Measured resistivity [Ohm*meter] | Calculated restivity [Ohm*meter] | Country
Wikinger wind farm. A wind farm located in the baltic region, just west of Bornholm. Several investigations on salinity where conducted and it was found that the lowest value translated into a calculated value of 0,91 |  | 0.91 | Germany
Svendborg havn, Anodes for a part of the harbour. The resistivity of the water were mesured at several locations, varying from 0,30 to 0,90. The 0,90 value is not applicable for the entire area since, it was measured near an outlet for a stream, and i was raining very heavy that day. So a value of 0,3-0,4 is applicable for Svendborg. | 0,3-0,4 |  | Denmark
Svendborgsund Bridge, several water samples taken during the installation of galvanic anodes. | 0.4 |  | Denmark
King Frederik IX bridge at Guldborgsund near Nykøbing Falster | 0.6 |  | Denmark
Izmit, Bridge located near Istanbul. The resistivity was measured at three locations in the spring. | 0.35 |  | Turkey
Copenhagen Harbour, Bridge over the harbour area. During the project the resistivity of the water was measured to 0,55. | 0.55 |  | Denmark
The Siøsund bridge, a bridge near the island of Funen. | 0.3 |  | Denmark
Copenhagen oilpier. | 0.28 |  | Denmark
Great belt, several measurements made at the west bridge of the great belt link. | 0,3-0,35 |  | Denmark
Fur and Branden harbour, two harbours located in Limfjorden in northen part of Jutland. | 0.3 |  | Denmark

## Current Density
Standard | Depth (m) | Temperature |  |  |  | Standard
DNV-RP-B401:2021 | "0-20" | Sub-Tropical "12-20c" |  |  |  | DNV-RP-B401:2021
Standard | Depth (m) | Temperature | Initial current density (mA/m2) | Mean current density (mA/m2) | Final current density (mA/m2) | Standard | Sediment initial current density (mA/m2) | Sediment mean current density (mA/m2)
DNV-RP-B401:2021 | "0-20" | Tropical ">20c" | 0.15 | 0.07 | 0.1 | DNV-RP-B401:2021 | 0.02 | 0.02
DNV-RP-B401:2021 | ">20-30" | Tropical ">20c" | 0.15 | 0.07 | 0.1 | EN 12495: 2000 | 0.025 | 0.02
DNV-RP-B401:2021 | ">30-100" | Tropical ">20c" | 0.12 | 0.06 | 0.08 | Norsok M-503: 2007 | 0.02 | 0.02
DNV-RP-B401:2021 | ">100-300" | Tropical ">20c" | 0.14 | 0.07 | 0.09
DNV-RP-B401:2021 | ">300" | Tropical ">20c" | 0.18 | 0.09 | 0.13
DNV-RP-B401:2021 | "0-20" | Sub-Tropical "12-20c" | 0.17 | 0.08 | 0.11
DNV-RP-B401:2021 | ">20-30" | Sub-Tropical "12-20c" | 0.17 | 0.08 | 0.11
DNV-RP-B401:2021 | ">30-100" | Sub-Tropical "12-20c" | 0.14 | 0.07 | 0.09
DNV-RP-B401:2021 | ">100-300" | Sub-Tropical "12-20c" | 0.16 | 0.08 | 0.11
DNV-RP-B401:2021 | ">300" | Sub-Tropical "12-20c" | 0.2 | 0.1 | 0.15
DNV-RP-B401:2021 | "0-20" | Temperate "7-12c" | 0.2 | 0.1 | 0.13
DNV-RP-B401:2021 | ">20-30" | Temperate "7-12c" | 0.2 | 0.1 | 0.13
DNV-RP-B401:2021 | ">30-100" | Temperate "7-12c" | 0.17 | 0.08 | 0.11
DNV-RP-B401:2021 | ">100-300" | Temperate "7-12c" | 0.19 | 0.09 | 0.14
DNV-RP-B401:2021 | ">300" | Temperate "7-12c" | 0.22 | 0.11 | 0.17
DNV-RP-B401:2021 | "0-20" | Artic "<7c" | 0.25 | 0.12 | 0.17
DNV-RP-B401:2021 | ">20-30" | Artic "<7c" | 0.25 | 0.12 | 0.17
DNV-RP-B401:2021 | ">30-100" | Artic "<7c" | 0.2 | 0.1 | 0.13
DNV-RP-B401:2021 | ">100-300" | Artic "<7c" | 0.22 | 0.11 | 0.17
DNV-RP-B401:2021 | ">300" | Artic "<7c" | 0.22 | 0.11 | 0.17
EN 12495: 2000 | "0-20" | North Sea (northern sector) above 62° N | 0.22 | 0.1 | 0.13
EN 12495: 2000 | ">20-30" | North Sea (northern sector) above 62° N | 0.22 | 0.1 | 0.13
EN 12495: 2000 | ">30-100" | North Sea (northern sector) above 62° N | 0.22 | 0.1 | 0.13
EN 12495: 2000 | ">100-300" | North Sea (northern sector) above 62° N | 0.22 | 0.1 | 0.13
EN 12495: 2000 | ">300" | North Sea (northern sector) above 62° N | 0.22 | 0.1 | 0.13
EN 12495: 2000 | "0-20" | North Sea (northern sector) 55°N to 62°N | 0.18 | 0.09 | 0.12
EN 12495: 2000 | ">20-30" | North Sea (northern sector) 55°N to 62°N | 0.18 | 0.09 | 0.12
EN 12495: 2000 | ">30-100" | North Sea (northern sector) 55°N to 62°N | 0.18 | 0.09 | 0.12
EN 12495: 2000 | ">100-300" | North Sea (northern sector) 55°N to 62°N | 0.18 | 0.09 | 0.12
EN 12495: 2000 | ">300" | North Sea (northern sector) 55°N to 62°N | 0.18 | 0.09 | 0.12
EN 12495: 2000 | "0-20" | North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands | 0.15 | 0.09 | 0.1
EN 12495: 2000 | ">20-30" | North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands | 0.15 | 0.09 | 0.1
EN 12495: 2000 | ">30-100" | North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands | 0.15 | 0.09 | 0.1
EN 12495: 2000 | ">100-300" | North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands | 0.15 | 0.09 | 0.1
EN 12495: 2000 | ">300" | North Sea (southern sector) below 55° N, West UK, West Ireland, Netherlands | 0.15 | 0.09 | 0.1
EN 12495: 2000 | "0-20" | Arabian Gulf, India, Australia, Brazil, West Africa | 0.13 | 0.07 | 0.09
EN 12495: 2000 | ">20-30" | Arabian Gulf, India, Australia, Brazil, West Africa | 0.13 | 0.07 | 0.09
EN 12495: 2000 | ">30-100" | Arabian Gulf, India, Australia, Brazil, West Africa | 0.13 | 0.07 | 0.09
EN 12495: 2000 | ">100-300" | Arabian Gulf, India, Australia, Brazil, West Africa | 0.13 | 0.07 | 0.09
EN 12495: 2000 | ">300" | Arabian Gulf, India, Australia, Brazil, West Africa | 0.13 | 0.07 | 0.09
EN 12495: 2000 | "0-20" | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia | 0.11 | 0.06 | 0.08
EN 12495: 2000 | ">20-30" | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia | 0.11 | 0.06 | 0.08
EN 12495: 2000 | ">30-100" | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia | 0.11 | 0.06 | 0.08
EN 12495: 2000 | ">100-300" | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia | 0.11 | 0.06 | 0.08
EN 12495: 2000 | ">300" | Mediterranean Sea, Adriatic Sea, Gulf of Mexico, Indonesia | 0.11 | 0.06 | 0.08
Norsok M-503: 2007 | "0-20" | North Sea (Up to 62 °N) | 0.2 | 0.1 | 0.13
Norsok M-503: 2007 | ">20-30" | North Sea (Up to 62 °N) | 0.2 | 0.1 | 0.13
Norsok M-503: 2007 | ">30-100" | North Sea (Up to 62 °N) | 0.17 | 0.08 | 0.11
Norsok M-503: 2007 | ">100-300" | North Sea (Up to 62 °N) | 0.19 | 0.09 | 0.14
Norsok M-503: 2007 | ">300" | North Sea (Up to 62 °N) | 0.22 | 0.14 | 0.17
Norsok M-503: 2007 | "0-20" | Norwegian Sea (above 62 °N) | 0.25 | 0.12 | 0.17
Norsok M-503: 2007 | ">20-30" | Norwegian Sea (above 62 °N) | 0.25 | 0.12 | 0.17
Norsok M-503: 2007 | ">30-100" | Norwegian Sea (above 62 °N) | 0.2 | 0.1 | 0.13
Norsok M-503: 2007 | ">100-300" | Norwegian Sea (above 62 °N) | 0.22 | 0.11 | 0.17
Norsok M-503: 2007 | ">300" | Norwegian Sea (above 62 °N) | 0.22 | 0.11 | 0.17

## Coating Breakdown
Depth (m) | Coating Category | Coating breakdown factor a | Coating breakdown factor b
"0-20" | "Category IV" | 0.02 | 0.008
Depth (m) | Coating Category | Coating breakdown factor a | Coating breakdown factor b
"0-20" | "Bare" | 1 | 0
">20-30" | "Bare" | 1 | 0
">30-100" | "Bare" | 1 | 0
">100-300" | "Bare" | 1 | 0
">300" | "Bare" | 1 | 0
"0-20" | "Category I" | 0.1 | 0.1
">20-30" | "Category I" | 0.1 | 0.1
">30-100" | "Category I" | 0.1 | 0.05
">100-300" | "Category I" | 0.1 | 0.05
">300" | "Category I" | 0.1 | 0.05
"0-20" | "Category II" | 0.05 | 0.025
">20-30" | "Category II" | 0.05 | 0.025
">30-100" | "Category II" | 0.05 | 0.015
">100-300" | "Category II" | 0.05 | 0.015
">300" | "Category II" | 0.05 | 0.015
"0-20" | "Category III" | 0.02 | 0.012
">20-30" | "Category III" | 0.02 | 0.012
">30-100" | "Category III" | 0.02 | 0.008
">100-300" | "Category III" | 0.02 | 0.008
">300" | "Category III" | 0.02 | 0.008
"0-20" | "Category IV" | 0.02 | 0.008
">20-30" | "Category IV" | 0.02 | 0.008
">30-100" | "Category IV" | 0.02 | 0.005
">100-300" | "Category IV" | 0.02 | 0.005
">300" | "Category IV" | 0.02 | 0.005

## Version History
Version | Date | Revisions | Prepared | Checked | Approved
1 | 2012-09-11 | First Issue | SAAY | JAJA | BBU
1.1 | 2014-12-19 | Sheet on seawater resistivity added and also user defined anode | JAJA | RSO | RSO
2.0 | 2016-06-17 | Updates of anodes and minor revisions | PHNI | RSO | RSO
3.0 | 01.12.2017 | Update of DNVGL standard, and added resistivity measurements. Error found in mean and current requirements, where the coating factor of steel in sediment was not included. Means that coated structures in sediment previusly has been calculated as bare steel. and therefore are on the conservative side. User defined anodes have been added in the anode data sheet. Error in some platforms anodes, where the 350 kg anode has been to long. | JAJA | RSO | RSO
4.0 | 10-22-2022 | Update of DNV standard with new coating breakdown factors and electrochemical capacity for anodes. Added mudline zone for surface areas and coating breakdown factor, removed surface area for sediment coated. | PHNI | JAJA | JAJA